DOI: https://dx.doi.org/10.18203/2394-6040.ijcmph20205195

Original Research Article

A study on water management strategies in a selected teaching hospital

Ayshathul Femitha*, Sunita Saldanha

Department of Hospital Administration, Yenepoya Medical College, Mangalore, Karnataka, India

Received: 16 September 2020

Revised: 01 November 2020

Accepted: 04 November 2020

*Correspondence:

Ayshathul Femitha,

E-mail: femithakcz@gmail.com

Copyright: © the author(s), publisher and licensee Medip Academy. This is an open-access article distributed under the terms of the Creative Commons Attribution Non-Commercial License, which permits unrestricted non-commercial use, distribution, and reproduction in any medium, provided the original work is properly cited.

ABSTRACT

Background: Water is a scarce and highly valuable natural resource. Hospitals require relatively large quantity of water and quality of water is equally important. Hospitals must focus on water efficiency and conservation measures in order to ensure the sustainable use of water. This study was undertaken to understand the current water management practices in the selected teaching hospital and to develop strategies for water conservation.

Methods: Descriptive study with observational method was used, to collect the data an observational checklist based on the guidelines of bureau of Indian standards (BIS) and world health organization (WHO) was developed. To observe and collect the data, uninformed visits was done to the Department of Maintenance on random days as per the convenience and the information was collected from standard operating procedures (SOPs) and records maintained in the department of maintenance and hospital infection control unit.

Results: The study found that a well-planned water supply system is present in the selected hospital to meet the required quantity of water. The study reveals that the total consumption of water per day in the hospital is higher than the BIS standards. Preventive and corrective maintenance of all the tanks, pipelines, plumbing, and equipment is done regularly. A well-organized system of quality control of water is present in the hospital and the grey water, is drained to sewage water treatment plant from where the water is recycled and reused.

Conclusions: Conservation of water enables hospitals to cut cost and to be proactive stewards of their community’s natural resources.

Keywords: Water management, Water consumption, Water quality, Water conservation, Water treatment

INTRODUCTION

Healthcare organization have a greater responsibility to effectively manage their individual water consumption, in an attempt to combat the water crisis. Hospitals have to focus on water efficiency and conservation measures in order to ensure sustainable use of water within hospital.1

Water plays an important role in safe healthcare delivery, it is used for various activities in a healthcare sector, from washing surgical tools and other equipment to creating a soothing environment for patients to have hydrotherapy. Lack of a water management system will directly impact the patient care, a poor water supply impacts health by causing acute infectious disease such as diarrhea or non-diarrheal disease which can arise from chemical substances such as arsenic and fluorides. Water is a scarce natural resource. It is the responsibility of every organization and individual to conserve water. As a major consumer of water, it is critical for the healthcare industry to adopt a proactive approach to conserving water.2

Water conservation technologies and strategies are often the most overlooked aspects of a whole-building design strategy such as large hospitals. However, many hospitals do not have an effective management for water consumption and planning replacements, such as pipes, valves etc. As natural resources such as water become increasingly scarce, managers often seek policies to reduce water demand. Water management is the activity of planning, developing, distributing, and managing the optimum use of water. The first step in water management is the identification of main water consumers and using policies for water consumption reduction while maintaining consumer’s well-being.3

This study was undertaken to understand the current water management practices in the selected teaching hospital, and to develop strategies for water conservation.

Methods

The following study is descriptive in nature and utilized an observational method conducted in Yenepoya medical college hospital from September 2019 to September 2020. An observational checklist based on WHO guidelines and BIS guidelines was developed for data collection. Additionally, uninformed visits to the department of maintenance were completed on random days as per the author’s convenience. The information such as data of water consumption for the past one year, working plan of water treatment plant, report of water quality test etc. was collected from SOPs and records maintained in the Department of Maintenance and the Hospital Infection Control unit. The findings of the study were then compared with the BIS and WHO guidelines and standards. Ethical approval for the study was received from the institutional ethics committee of Yenepoya medical college. No statistical analysis was conducted. To understand the consumption of water, data of one year was analyzed retrospectively and then the actual demand of water was calculated based on BIS. Water conservation methods are then suggested based on the findings of the study.

Results

To study the consumption of water, retrospective data for one year was collected and analyzed. The data indicates that total water consumption per day for the hospital was 3,37,664 L (Table 1), according to BIS standards per day requirement is 2,32,210 L per day which includes drinking water, sanitation, hand washing and flushing but excludes dietary and laundry and linen. This highlights that the hospital utilizes about 105,454 additional liters of water compared to the average BIS standards.

To meet the daily water requirement a well-planned water supply system is in place (Figure 1). Deep borewells are the main source of water supply, and they are recharged through rooftop rainwater harvesting. In addition to this there is one water reservoir available through rainwater harvesting. In addition, memorandum of understanding (MoU) with an external water supply agency is established as per the joint commission on the accreditation of healthcare organizations, (JCAHO), as a provision for any contingencies.4 It was found that regular maintenance of all the equipment like plumbing, pipelines etc. is conducted. Preventive maintenance checklist is available and completed as scheduled. However, the author noted that the activities completed during preventive maintenance are not documented. The documentation of such activities will be useful to understand the type of problem and its frequency which will help to analyze the root cause of the issue and to take appropriate preventive action. Complaints are raised through the hospital information system subject to which immediate corrective action are taken. Wherever applicable annual maintenance is completed with the equipment such as water treatment plant, RO plant etc.

Table 1: Water usage for one year (January to December 2019).

| Month of consumption | Usage (kl) | OP | IP | IP+ OP |
| --- | --- | --- | --- | --- |
| January 2019 | 9433 | 18801 | 22462 | 41,263 |
| February 2019 | 8355 | 17748 | 20156 | 37,904 |
| March 2019 | 9253 | 18688 | 23255 | 41,943 |
| April 2019 | 9616 | 17974 | 22540 | 40,514 |
| May 2019 | 9243 | 17207 | 23051 | 40,258 |
| June 2019 | 10352 | 17810 | 23132 | 40,942 |
| July 2019 | 10978 | 21943 | 26219 | 48,162 |
| August 2019 | 10184 | 19377 | 22690 | 42,067 |
| September 2019 | 11331 | 21500 | 25084 | 46,584 |
| October 2019 | 10883 | 21892 | 25446 | 47,338 |
| November 2019 | 11006 | 20469 | 22357 | 42,826 |
| December 2019 | 10925 | 17590 | 21565 | 39,155 |
| Total | 1,21,559 | 2,49,069 | 2,99,066 |  |

Relatively inexpensive and simple technology like regular assessment of water quality can have a high impact in hospital infection control. Microbes present in water pose a significant health risk to patients and care providers. Ensuring water supply of adequate quality and quantity is essential for health. Chemical parameters of water quality are checked every month (Table 2) and biological parameters of water quality (Table 3) are checked once in three months as per WHO standards before consumption.5 Microbiological analysis (Table 4) and endotoxin level test (Table 5) of dialysis water is done separately according to AAMI standards.6 The chemical parameters were in accordance with the BIS standards.7 The microbial growth was found three times in drinking water during the study period, and corrective action such as thorough cleaning of water tank and servicing of aqua filter conducted.

Table 2: The assessment of the chemical parameters of water.

| Parameter | Acceptable amount | October | November | December |
| --- | --- | --- | --- | --- |
| Essential characteristics |  |  |  |  |
| Color | No obvious color | No obvious color | No obvious color | No obvious color |
| Odour | No odour | No odour | No odour | No odour |
| Taste | No peculiar taste | No peculiar taste | No peculiar taste | No peculiar taste |
| Turbidity | No turbidity | No turbidity | No turbidity | No turbidity |
| pH | 6.5-8.5 | 7.15 | 7.48 | 7.05 |
| Chloride (mg/l) | 250-1000 | 20 | 20 | 20 |
| Residual chlorine (mg/l) | 0.2 | 0 | 0 | 0 |
| Total hardness (mg/l) | 300-600 | 130 | 80 | 70 |
| Desirable characteristics |  |  |  |  |
| Fluoride (mg/l) | 1.5-1.9 | 0 | 0 | 0 |
| Total dissolved solids (mg/l) | 500-2000 | 0 | 0 | 40 |
| Total suspended solids (mg/l) | 500-2000 | 80 | 0 | 160 |
| Total viable count (cfu/ml) | <500 | 0 | 420 | 20 |
| Total solids (mg/l) | 500-2000 | 120 | 0 | 200 |

Table 3: Microbial analysis of water collected from different areas.

| Variables | Retrospective |  | Prospective |  |
| --- | --- | --- | --- | --- |
| Site of collection | Report (March 2019) | Report (June 2019) | Report (September 2019) | Report (December 2019) |
| Physiotherapy | No growth of coliforms | No growth | Growth of coliforms | No growth |
| 7th a ward | No growth | No growth | No growth | No growth |
| NICU | No growth | Growth | No growth | No growth |
| 8th floor | No growth | No growth | No growth | No growth |
| 6th OT | No growth | Growth | No growth | No growth |
| SICU | No growth | No growth | No growth | No growth |
| Casualty | No growth | Growth | No growth | No growth |
| 1 floor | No growth | No growth | Growth | No growth |
| 5 old building | No growth | Growth | No growth | No growth |
| 5E | No growth | No growth | No growth | No growth |
| 4E | No growth | No growth | No growth | No growth |
| 4thold building | No growth | Growth | No growth | No growth |
| POR | No growth | No growth | No growth | No growth |
| Cafeteria | No growth | No growth | No growth | No growth |
| 6th E | No growth | No growth | No growth | No growth |
| 2nd floor old building | No growth | No growth | No growth | No growth |
| 3rd OT | No growth | No growth | No growth | No growth |
| 1st floor | No growth | Growth | No growth | No growth |
| 3A | No growth | No growth | No growth | No growth |
| 3C | No growth | Growth | Growth | Growth |
| CSSD | No growth | No growth | No growth | No growth |
| Radiology | No growth | Growth | No growth | No growth |
| LT | No growth | No growth | No growth | No growth |
| 3B | No growth | Growth | No growth | No growth |
| 7E | No growth | Growth | No growth | No growth |

Table 4: Microbial analysis of RO water of dialysis unit.

| Retrospective | Date | Microbial growth |
| --- | --- | --- |
|  | 4/1/2019 | No growth |
|  | 21/1/2019 | No growth |
|  | 28/1/2019 | No growth |
|  | 4/2/2019 | No growth |
|  | 10/3/2019 | No growth |
|  | 18/3/2019 | Growth (Acinetobacter baumani) |
|  | 25/3/2019 | No growth |
|  | 1/4/2019 | No growth |
|  | 8/4/2019 | No growth |
|  | 22/4/2019 | No growth |
|  | 29/4/2019 | No growth |
|  | 6/5/2019 | No growth |
|  | 13/5/2019 | Growth (Staphylococcus species) >200 TVC |
|  | 21/5/2019 | No growth |
|  | 28/5/2019 | No growth |
|  | 5/6/2019 | No growth |
|  | 10/6/2019 | No growth |
|  | 18/6/2019 | No growth |
|  | 29/6/2019 | No growth |
|  | July | - |
| Prospective | 5/8/2019 | No growth |
|  | 2/9/2019 | No growth |
|  | 7/10/2019 | No growth |
|  | 14/10/2019 | No growth |
|  | 21/10/2019 | No growth |
|  | 4/11/2019 | Growth (Klebsiella species) |
|  | 11/11/2019 | No growth |
|  | 16/11/2019 | No growth |
|  | December | - |

The RO plant pumps only ultrapure water and almost 50-70% of water that goes into the plant is wasted and is drained into the sewage. The excess grey water from the hospital is transported to sewage water treatment plant from where the water is recycled and reused. Inflow to the sewage treatment plant is about 4-5 lakhs of liters per day out of which 50-60% of recycled water is used for activities such as flushing, and gardening and the rest is used for irrigation.

Table 5: Endotoxin assessment of RO water.

| Month | Endotoxin level (EU/ml) | Result |
| --- | --- | --- |
| February | >0.25 | Does not complies |
| May | >0.25 | Does not complies |
| August | >0.25 | Does not complies |
| November | >0.25 | Does not complies |

Discussion

The study reveals that the consumption of water in the hospital was higher than the average standards. Collett et al found that the water consumption in their hospital was 200,000 L per day for 183 beds, where the standard requirement was 82,350 L per day.8 Another study by Abbassi et al reported higher water consumption about 8-200 times higher than actual water demand and reported it could be due to traditional distribution system and improper management, in this study the higher consumption can be attributed to additional usage for clinical and nonclinical purposes such as dialysis, super specialty services, construction works, individual usage like surgical scrub as similar to findings from the study by Petterwood et al etc.3,9

In this study it was found that a MoU is established with an external source of water supply this was in accordance with the JCAHO standards and similar practice was observed in other studies. A study conducted by Guibourg et al emphasizes the requirement of emergency water supply, after encountering an emergency in which the entire water supply was polluted due to construction damage to the public water system.10 Another study conducted by Canan et al explored the capabilities of healthcare facilities regarding water supply for emergency purposes, and found that the emergency water supply capability can be improved through collaboration with local emergency preparedness organizations, construction of water towers on or near hospital grounds, and the use of synergetic water reservoir capacity.4

RO plant 1

Raw water: deep borewells/reservoir

water treatment plant

overhead tanks with capacity

- 90000 L

- 40000 L

Cleaning, washing and bathrooms

RO plant 2

Pumped into the sump

Water tank (1000L)

Water tank (600L)

Dialysis

CSSD, OT, drinking

Figure 1: Flowchart of water supply plan.

This study shows there was a facility of roof top rainwater harvesting in the hospital. Similar practice of rainwater harvesting was presented in a case study from Warragul hospital, where 137 kiloliters tank was built to store the rainwater for the using as boiler feed water in laundry, the study showed that the hospital obtained an annual saving of 1,967 kiloliters of water and a 25 per cent reduction in boiler feedwater treatment chemicals.11

The chemical and biological parameters of water quality was checked in the hospital before consumption and it was found that the parameters were in accordance with the standards. Conversely, the results from a quality test conducted by Collet et al, concluded that RO water and raw water were found to have total hardness (as calcium carbonate), total dissolved solids (TDS) and Endotoxin level exceeding that of required standards.8 Skarupskiene  et al in 2007 and found that the endotoxin level of both dialysate fluid and dialysate water was well within the standard in several hemodialysis centres of different Lithuanian cities, two samples indicated the level >0.03 EU/ml but all samples indicated level were less than <0.25 EU/ml.12 When the same study conducted in 201014, it was found that water from 8% of dialysate centres did not meet required standards.13 The study concluded with recommendations for continuous monitoring on endotoxin level in dialysate water within Lithuanian cities.

The RO plant pump only ultrapure water to the specific department and almost 50-70% of water that goes into the plant was wasted and was drain to the sewage. The sewage water was recycled and reused. Inflow to the sewage treatment plant is about 4-5 lakhs per day out of which 50-60% of recycled water is used for activities such as flushing, and gardening and the rest is used for irrigation. A case study done from Warragul hospital indicated that the hospital management had adopted a practice of reusing the RO ejected water to sterilizer vacuum pump and condenser cooling and water was then drained to sewage and after treatment was used in flushing system, saving about 33% of total water consumption.

COnclusion

The present study reveals a satisfactory practice of water management in the selected teaching hospital with a well-organized water supply, quality control and maintenance system. In addition, the water management strategies like benchmarking, water audit, water efficiency fixtures, leakage detection techniques and water conservation campaign may assist further in improving the water conservation and may ultimately alleviate future demand for water.

Funding: No funding sources

Conflict of interest: None declared

Ethical approval: The study was approved by the Institutional Ethics Committee

References

Priyalal WG, De Silva ML, Rajini PA. A study on water management strategies practiced in healthcare facilities: A literature review. In: 6th International Conference on Engineering and Construction Management. 2015. Available from: www. civil. mrt.ac.lk/conference/ICSECM_2015/book_3/Extract/SECM-15-032. pdf 2015. Accessed on 10 August, 2020.

Hunter PR, MacDonald AM, Carter RC. Water supply and health. PLoS med. 2010;7(11):e1000361.

Abbasi F, Samaei MR, Mehdizadeh A. The Main Challenges and Suggested Solutions for Optimization of Water Management in an Educational hospital. J Environ Heal Sustain Develop. 2018;3(3):585-92.

Canan C. An Examination of the Emergency Water Supply of Healthcare Facilities in Southeast Louisiana. Springer. 2017;2.

Water S. World Health Organization. Guidelines for drinking-water quality: incorporating first addendum. Vol. 1, Recommendations. Available at: https://apps.who.int/iris/bitstream/handle/10665/204411/9789241547611_eng.pdf;jsessionid=BBC07CEAA70AD00F12114B89C9332F6C?sequence=1. Accessed on 10 August 2020.

ANSI/AAMI/ISO. Guidance for the preparation and quality management of fluids for hemodialysis and related therapies. Association for the Advancement of Medical Instrumentation; Arlington, VA. 2011;23500. Available at: https://dialysiswatersolution.com/regulations-and-guidelines/ansiaami/ansiaami-23500-guidance-for-the-preparation-and-quality-management-of-fluids-for-hemodialysis-and-related-therapies. Accessed on 10 August 2020.

Bureau of Indian Standards. Drinking Water-Specification (Second Revision). IS 10500: 2015. New Delhi. Available from: http://cgwb.gov.in/Documents/WQ-standards.pdf. Accessed on 10 August, 2020.

Collett S, Samarin I, Bhalchandra R, Soundaranayagam JR, Garai S, Chandy M et al. Water usage in a multi-speciality hospital and its effective management. J Academy Clin Microbiol. 2016;18(2):135.

Guibourg S, Moalic E, Baron R, Saliou P. Emergency management of water supply pollution in a French teaching hospital. Infect Cont Hospital Epidemiol. 2019;40(10):1207-9.

Guibourg S, Moalic E, Baron R, Saliou P. Emergency management of water supply pollution in a French teaching hospital. Infection Control Hospital Epidemiology. 2019 Oct; 40(10):1207-9.

West Gippsland Healthcare Group. Greening Our Hospitals: Water. Case study-Rainwater harvesting for boiler feedwater and using water three times. Available from: http://greening-westgipps%20-%20PDF.pdf. Accessed on 10 August, 2020.

Skarupskiene I, Bumblyte IA, Kuzminskis V. The level of endotoxins in hemodialysis water and dialysate. Medicina (Kaunas, Lithuania). 2007;43(l)1:81-4.

Skarupskienė I, Bumblytė IA, Tamošaitis D, Venterienė J, Kuzminskis V. The level of endotoxins in hemodialysis water and dialysate in Lithuanian hemodialysis centers. Medicina. 2010;46(8):556.

Cite this article as: Femitha A, Saldanha S. A study on water management strategies in a selected teaching hospital. Int J Community Med Public Health 2020;7:5120-5.